[image: image1.emf]
             BARD MANUFACTURING COMPANY, INC. 
          


QC501 Series Chilled Water A/C
Engineering Specification Guide

1.0
GENERAL

Furnish and install a self-contained, vertical, floor standing, chilled water air conditioner be manufactured by Bard Manufacturing Company, Inc.  The unit shall be approved and listed by Intertek ETL listed (ETL US/C).  Unit shall be factory assembled,  pre-wired, tested and ready to operate.  Unit shall include 5 year parts warranty covering parts, and heat transfer coils, subject to terms and conditions of Bard Limited Warranty agreement.

Manufacturers: Capacities shall be as indicated on drawings and units shall be manufactured by Bard Manufacturing Company, Inc. or prior approved equal.

2.0
CONSTRUCTION FEATURES

2.1
CABINET

Constructed of 20 gauge pre-painted or vinyl laminated galvanized steel.  Choices available are either two-tone (vinyl) finish with “slate” front panels and “platinum” cabinet for designer appearance,  (gray) or (beige) painted steel (select one).  Vinyl finish is very resistant to scratching and marring and is easy to clean.  Tamper resistant fasteners are provided for access panels.  Unit includes built-in rollers for each installation into wall sleeve and removal for service, if necessary.  Front panel is hinged and lockable for filter service and access to primary functional electrical controls.

2.2
INSULATION
Cabinet is fully insulated with foil covered, high density fiberglass insulation with sealed edge treatment and special sound deadening insulation material in the compressor section.  All insulation is designed to resist mold and mildew growth and facilitate ease of cleaning.

2.3
Water coil and control valves
Water coil shall be constructed of copper tubes and aluminum fins, with two circuits, providing 2-stages of control. Either 2-way or 3-way valves are available for field installation.
2.4
CONDENSATE DRAIN SYSTEM
Condensate shall be removed from the unit by connections located in the back or side of the unit.  The chilled water coil shall have a stainless steel drain pan to eliminate corrosion.
2.6
INDOOR BLOWER MOTOR
The indoor blower motor shall be a variable speed (ECM) type to produce the same rated air flow from 0 to .8 inch WC of external static pressure.  The motor is to be self adjusting to provide proper rated air flow at high static pressures without user adjustment or wiring changes by the user.  The motor shall be programmed for 20-second ramp up and 60-second down rate for quiet, smooth starting and stopping. PSC motor shall not be acceptable.

2.7
ELECTRICAL COMPONENTS
Electrical components are easily accessible for routine inspection and maintenance through front service panels.  Circuit breaker is standard on all models. Available voltages are 208/230 single phase and 115 volt single phase. Circuit breaker access is through lockable access panel.  Lock and key are provided as standard equipment.  Unit shall have single point entry for line voltage.

2.8
CONTROL CIRCUIT

The internal control circuit shall consist of a current limiting 24VAC type transformer. 
3.0
HEAT OPTIONS (Select One)

3.1
None

3.2
Electric Heat

The heat pump shall have a factory installed electric resistance heater available that is designed specifically for application in the Q-Tec Series unit.  Heater shall include automatic limit safety controls.





3.3
 HOT WATER COIL
The hot water coil shall be factory mounted in discharge air plenum, or for ducted application, coil is complete with 3-way valve (field installed) and can be wired for first or second stage heat.

4.0
VENTILATION OPTIONS (Select One)

Q-Tec models are designed to provide optional ventilation packages to meet all of your ventilation and indoor air quality requirements.  All ventilation packages are factory installed. Ventilation options require wall sleeve and louver, and unit location on exterior wall.
4.1
BAROMETRIC FRESH AIR DAMPER

      STANDARD
The barometric fresh air damper is a standard feature on all models.  It allows outside ventilation air, up to 25% of the total air flow rating of the unit, to be introduced through the air inlet openings and to be mixed with the conditioned air.  The damper opens during blower operation and closes when the blower is off.  Adjustable blade stops allow different amounts of outside air to be introduced into the building and can be easily locked closed if required.


4.2
BLANK OFF PLATE




       OPTIONAL
A blank off plate covers the air inlet openings which restrict any outside air from entering the unit.  The blank off plate should be utilized in applications where outside air is not required to be mixed with the conditioned air. With blank off plate option unit can be located anywhere in the space.
4.3
COMMERCIAL ROOM VENTILATOR

        OPTIONAL
The built-in commercial room ventilator is internally mounted and allows outside ventilation air, up to 50% of the total air flow rating of the unit, to be introduced through the air inlet openings.  It includes a built-in exhaust air damper.  The commercial room ventilator (CRV) shall be easily removed for maintenance or replacement.  The damper can be easily adjustable, to control the amount of fresh air supplied into the unit.  The CRV can be controlled by indoor blower operation or field controlled based on room occupancy or schedule.  Unit complies with ANSI/ASHRAE Standard 62.1 Ventilation for Acceptable Air Quality.

Two Models Available (select 1):
Spring Return on Power Loss or Deactivation - Vent Option V

Power Return (will not close on power loss) –  Vent Option P

4.4
ENERGY RECOVERY VENTILATOR

       OPTIONAL
The Energy Recovery Ventilator (ERV) shall consist of 1 or 2 rotary wheels in an insulated cassette frame with seals, drive motor and belt. The ERV assembly shall also include intake and exhaust blowers. The entire assembly shall easily slide in or out of the ventilation section, allowing for maintenance or replacement. The total energy wheel shall be coated with silica gel desiccant, permanently bonded without the use of binders or adhesives. The coated segments shall be washable with detergent or alkaline coil cleaner and water. Desiccant shall not dissolve or deliquesce in the presence of water or high humidity.  All diameter and perimeter seals shall be provided as part of the cassette assembly and shall be factory set. Drive belts shall not require external tensioners or adjustment. Cassette wheels shall include rims to prevent belts from slipping off wheels.   Intake and exhaust blowers shall have selections of high, medium or low speed and selected independently, to allow for positive pressurization if desired. The ERV cassette including parts and media shall include 5year warranty subject to terms and conditions of Bard’s warranty.
The ERV thermal performance shall be certified by the manufacturer in accordance with ASHRAE Standard 84, Method of Testing Air-to Air Heat Exchangers and ARI  Standard 1060, Rating for Air-to-Air Energy Recovery Ventilation Equipment Cassettes, and shall be listed in the ARI Certified Products. Unit complies with ANSI/ASHRAE Standard 62.1 Ventilation for Acceptable Air Quality.

5.0
FILTER OPTIONS - (Select One)

5.1
1” Fiberglass

5.2
2” Fiberglass – Pleated – MERV 6

7.0
CABINET COLOR – (Select One)

7.1
Washable Vinyl  -  Two-Tone Finish

7.2
Slate Gray

7.3     Beige

8.0
COIL OPTIONS – (Select Standard Hydrophilic coated indoor coil)
10.0
ACCESSORIES


10.1
WALL SLEEVE 
        (Wall sleeve and louver required for ventilation options)
Wall sleeve shall be factory supplied and must be constructed of 16 gauge galvanized steel, coated with an epoxy primer and baked-on polyester enamel paint.  It shall be designed to withstand a minimum of 1000 hours of salt spray protection when tested per ASTM B117-03 standard.  

10.2
Furnish factory louver designed for ventilation (outside) air intake and exhaust.  Louver shall be aluminum construction with removable core for service.  Access to removable core is by tamper-proof screws. Louver shall have a powder coat finish.  See our color chart for color selections.

10.3
AIR DISTRIBUTION – (Select 1)
10.3.1
The Q-Tec shall have a discharge air plenum with double deflection register mounted on front.

10.3.2
The Q-Tec shall have a discharge air plenum with double deflection supply register on the front and both sides.

10.3.3  
The Q-Tec shall be ducted with a cabinet extension to cover ductwork

11.0
WARRANTY

11.1
The Bard product specified shall be free from defects in materials and workmanship for a period of 5 years  for a period of 5 years for all parts. Warranty period shall start from date of installation as stated on warranty card; or from date of shipment if no warranty card is returned to Bard Manufacturing.  Equipment must be used under normal conditions and warranty is subject to Bard Manufacturing’s standard limited warranty statement. 

12.0
INSTALLATION

12.1
Installation shall be done in strict adherence to Bard’s Installation Instructions.

F1916 (2010 02)



Page 1 of 5

